| QUALITY AND PERFORMANCE SCRUTINY COMMITEE | 2 nd September 2002 | PART 1 (OPEN TO THE PUBLIC) |
| --- | --- | --- |
| SUBJECT: ENERGY MANAGEMENT ACTIVITY DURING THE PERIOD JUNE 2002 TO AUGUST 2002. |  |  |
| REPORT OF: DIRECTOR OF CORPORATE SERVICES |  | FOR INFORMATION |

- REPORT SUMMARY

- PURPOSE OF REPORT:

To update members on matters arising since the June 2002 meeting of the Quality and Performance Scrutiny Committee and to report significant activities in the Energy Audit Group.

- RECOMMENDATIONS

Members are asked to note the level of savings being achieved and identified by the Group.

- ROUTING

Direct to council.

- IMPLICATIONS

4.1	Resources (Finance/Staffing):		The operation of an efficient Energy

Management Group contributes to considerable

Cost savings to the City Council. Competitive

Tendering for energy supply will minimise the

Strain on limited budgets.

4.2	Performance Review:			Not Applicable.

4.3	Environmental:			Reduction in the use of fuels, energy and water

will minimise harmful effects on the

environment.

4.4	Equal Opportunities:			Not Applicable.

4.5	Community Strategy:			Not Applicable.

4.6	Anti-Poverty Strategy:		Not Applicable

| IF YOU HAVE ANY QUERIES PLEASE CONTACT Jim Gosney 793 3472 | BACKGROUND DOCUMENTS |
| --- | --- |
| QUALITY CONTROL | Report Prepared by Jim Gosney 793 3472 Checked by Donald Simpson 793 3290 |
| Corporate Services (Finance), Salford Civic Centre, Chorley Road, Swinton. M27 5AW |  |

# REPORT DETAILS

- ENERGY MANAGEMENT

Activities undertaken during the period June 2002 to August 2002 include the following: -

Progress of the energy audit plan

The levels of energy savings achieved.

Climate Change Levy Exemption for Schools

- ENERGY PERFORMANCE

Of the 43 local authorities in the North West, Salford is one of only eight to achieve and exceed the government national target of an average of a 2% reduction in consumption per annum.

The average annual improvement has been achieved by investment in energy efficient controls and a pro-active energy audit team.

Over the past six years £2.7 million have been saved. The environmental benefits of this reduction in harmful emissions equates to 2,268 tonnes of carbon dioxide.

Salford has the highest annual average improvement of the Greater Manchester Local Authorities and is currently seventh in the North West League Table. See Appendix B.

- ENERGY SAVINGS ACHIEVED

Implemented Energy Savings, through purchasing, tariff analysis and water audits amount to £97,743 for the year to date. Refunds for the amount of £122,133 have also been achieved and cheques from the various suppliers received.

A number of energy audits at the following premises have also been conducted.. The summaries are attached in Appendix A.

Premise Name				Potential Savings (Annual)		CO2 Tonne

Cannon Williamson High School				£3,665				52.0

St Ambrose Barlow High School				£4,955				52.0

Irlam Primary School						£1,905				-

Civic Centre							£4,870				61.0

---------				-------

£15,395			165.0

In addition to the above, there are ongoing energy audits at Broughton Resource Centre, Irlam Council Offices, Winton and Belvedere Early Years Centre.

8.	CLIMATE CHANGE LEVY EXEMPTION AT SCHOOLS

As Members may be aware, the climate Change Levy (CCL) tax was introduced on the 1st April 2001, resulting in increases of 12 to 20% on most of the council’s premises electricity and gas invoices.

To make the administration of collecting the tax as simple as possible, Customs and Excise have linked the right to collection to the VAT status of the end user. For example, if you pay the full rate VAT (17.5%) CCL will be collected. If you pay domestic rate (5%), you will be exempt from CCL.

HM Customs and Excise have confirmed that all Voluntary Aided and Voluntary Controlled Schools are accepted as a charity and, therefore, should benefit from the reduced rate of VAT, resulting in the exemption from Climate Change Levy. The savings resulting from this exercise will amount to approximately £30,325.

.

9.	ENVIRONMENTAL BENEFITS OF ENERGY AUDIT ACTIVITIES

| Premises | Date Report Issued | Potential Savings (Annual) | CO2 Reduction (Tonnes) |
| --- | --- | --- | --- |
| Seedley Primary School | 01/03/01 | £4,646 | 9.29 |
| Langworthy Rd Primary School | 26/03/01 | £2,940 | 5.88 |
| St Pauls C E Primary School | 01/06/01 | £3,350 | 6.70 |
| St Marks R C Primary School | 18/06/01 | £3,395 | 6.8 |
| Monton Green Primary School | 27/06/01 | £2,480 | 4.96 |
| Libraries | 03/08/01 | £23,629 | 47.3 |
| Christ The King RC Primary | 10/08/01 | £3,608 | 7.2 |
| St Gilberts RC Primary | 27/03/02 | £1,843 | 36.9 |
| Lower Kersal PS | 22/05/02 | £9,512 | 11.9 |
| Lark Hill Primary | 23/05/02 | £5,365 | 10.73 |
| St Lukes Primary | 23/05/02 | £2,040 | 4.08 |
| St Boniface RC Primary | 23/05/02 | £1,360 | 2.72 |
| Cannon Williamson | 11/07/02 | £3,665 | 52.0 |
| Civic Centre | 14/08/02 | £4,870 | 61.0 |
| St Ambrose Barlow High | 11/07/02 | £4,955 | 52.0 |
| Irlam Primary School | 18/07/02 | £1,905 | - |
|  |  | £79,563 | 319.46 |

APPENDIX A

IRLAM PRIMARY SCHOOL

| Description of Recommendation | Annual Saving (£) | Estimated Cost of Implementation (£) | Pay Back Period (Years) |
| --- | --- | --- | --- |
| Install 24 no. WC Dams | £ 96.50 | £ 132.00 | 16 Months |
| Install 62 no. Push Taps | £830.80 | £ 1116.00 | 16 Months |
| Install 2 no. Occupancy Sensing Urinal Controls | £977.82 | £ 450.00 | 5.5 Months |
|  | £1905.12 | £1698.00 | 10.7 Months |

THE CIVIC CENTRE

| 1.3.1 No Cost Measures |  |  | Saving kWh | Saving £ | CO2 Tonne |  |
| --- | --- | --- | --- | --- | --- | --- |
| .1 | Ph 2 – reduce pre-heater set point from 20°C to 17°C in Summer |  | 6,200 gas | 100 | 1.6 |  |
| .2 | Ph 1 – change Trend software to allow Eco off to be 15°C |  | 500 elect 3,400 gas | 75 | 1.1 |  |
|  | Total No Cost Measures |  |  | £175 |  |  |

| 1.3.2 Low Cost Measures (in order of payback up to £6,000) |  | Budget Cost £ | Saving kWh | Saving £ | CO2 Tonne | Payback Years |
| --- | --- | --- | --- | --- | --- | --- |
| .1 | Ph 2 – Induction unit pump control | 350 | 16,500 elect | 615 | 7.1 | 0.6 |
| .2 | Ph 2 - Coke vending machine – time control | 40 | 700 day 750 night | 50 | 0.6 | 0.8 |
| .3 | Ph 2 – Boiler control | 350 | 22,100 gas | 360 | 5.6 | 1.0 |
| .4 | Ph 2 – Boiler flow compensation | 150 | 6,300 gas | 100 | 1.6 | 1.5 |
| .5 | Ph 3 – Boiler flow compensation | 150 | 6,000 gas | 95 | 1.5 | 1.6 |
| .6 | Ph 3 – Ventilation plant – night pre-cooling | 200 | 3,200 elect - 1,100 night | 120 | 1.4 | 1.7 |
| .7 | Ph 1 – Hot water control | 250 | 9,000 gas | 145 | 2.3 | 1.7 |
| .8 | Ph 2 – Ventilation plant – night pre-cooling | 200 | 2,600 elect - 700 night | 95 | 1.1 | 2.1 |
| .9 | Ph 2 – North stairwell - radiator TRV | 50 | 1,100 gas | 20 | 0.3 | 2.5 |
| .10 | Power regulators on refrigerators | 75 | 525dy 150 ni | 25 | 0.3 | 3.0 |
| .11 | Architectural services – heating control | 850 | 16,50 gas | 270 | 4.2 | 3.1 |
| .12 | Ph 3 – Ventilation Plant cooler battery - relocation in supply air duct | 1,500 | 8,100 elect | 300 | 3.5 | 5.0 |
| .13 | Ph 2 – Ventilation Plant fans - Variable speed control | 4,000 | 18,200 elect | 675 | 7.8 | 5.9 |
| .14 | Ph 3 – Ventilation Plant fans - Variable speed control | 5,500 | 21,400 elect | 795 | 9.2 | 6.9 |
|  | Total Low Cost Measures | £13,665 |  | £3,665 | 46.5 tonnes | 3.7 years |

| 1.3.3 High Cost Measure (above £6000) |  | Budget Cost £ | Saving kWh | Saving £ | CO2 Tonne | Payback Years |
| --- | --- | --- | --- | --- | --- | --- |
| .1 | Ph 2 – Replacement of old fittings | 7,560 | 27,720 elect | 1,030 | 11.9 | 7.3 |

| 1.3.4 Summary - all measures |  | Budget Cost £ | Saving kWh | Saving £ | CO2 Tonne | Pay-back |
| --- | --- | --- | --- | --- | --- | --- |
|  | Total | £21,225 | 100,345 elect 70,600 gas | £4,870 | 61.1 | 4.4 years |

## Performance Indicators (NPI) and the Environment

The Department of the Environment’s energy efficiency office publish energy performance indicators for a range of buildings.  These provide a single measure of building performance expressed in terms of kWh/m2 and carbon dioxide C02.  To allow for varying annual conditions these are adjusted for regional degree days (a measure of how long the ambient is below a base temperature of 15.5oC) and occupancy time.  These figures are called Normalised Performance Indicators or NPI.  The calculation is detailed in appendix V.  Most of the areas are air conditioned but the Phase 1 Town Hall building is heated by radiators and naturally ventilated, however the highly serviced computer centre offsets this so the NPI yardstick is used for a standard air conditioned office building.

| The Civic Centre Performance Indicators |  | 2001/2002 data |  | National (DEFRA) Standards Offices Air conditioned - standard |  |  | Treated Area 10,937 m2 Occupants |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Energy Cost Performance (excluding water) | Current |  | Poor above |  | Good below | Projected NPI improvement |  |  |  |
| Cost per square metre | £ 3.84 m2 |  | £14.20 |  | £8.00 | £ 3.42 m2 |  | 10.9% |  |
| Cost per occupant | £ 44.73 |  | £15.26 |  | £11.07 | £ 39.85 |  |  |  |
| Energy Performance (NPI) |  |  |  |  |  |  |  |  |  |
| Gas | 120 kWh/m2 |  | 178 |  | 97 | 111 kWh/m2 |  | 7.5% |  |
| Electricity | 51 kWh/m2 |  | 226 |  | 128 | 43 kWh/m2 |  | 15.7% |  |
| Environmental Performance |  |  |  |  |  |  |  |  |  |
| CO2 tonnes per year (coal equivalent) | 490.2 tonnes |  | n/a |  | n/a | 429.2 tonnes |  | 11.9% |  |
| CO2 kilograms / m2 | 42 kg/m2 |  | 154 |  | 86 | 37 kg/m2 |  |  |  |

## Projected Utility Cost Savings

| Utility Costs | 2001/02 | Average pence /kWh | £/m2 | Projected saving £ | % |
| --- | --- | --- | --- | --- | --- |
| Electricity | £32,968 | 5.5249 | 2.84 | £3,725 | 11.3% |
| Gas | £11,629 | 0.946 | 1.00 | £1,145 | 9.8% |
| Metered Water | £ 7,238 | 132.01 p/m3 | 0.62 | £0 | 0 |
| Totals | £51,835.00 |  | £4.46 | £4,870.00 | 9.4% |

# Tariffs, Plant and Buildings

## Gas - heating / hot water

Costs for the competitively tendered 2001/2002 contract (Shell Gas direct), were £11,629 based on advised annual cost data giving an average of 0.946p/kWh.

The current cost is 1.062p/kWh.  Due to modest boiler heat losses (please see appendix IV) plus distribution mains losses the seasonal heating system efficiency is estimated to be a good 75%. The actual fuel cost in use is 1.62p/kWh.  A Climate Change Levy (CCL) of 0.15p/kWh has been applied since April 2001.

The major observation is that whilst gas costs have increased kWh consumption has decreased which is excellent in view of the Phase 3 electrode boilers being replaced with gas boilers.

## Electricity

Costs for the competitively tendered 2001/2002 contract were £32,968, giving an average of 5.5249 p/kWh including the CCL charge of 0.43p/kWh from 1st April 2001 to January 2002.

From February 2002 the contract has be re-tendered and awarded to London Electricity under a green energy contract which avoids the CCL.

The current unit rates are a good 3.72p/kwh day and 2.76p/kWh night with supply capacity at £1.00 / kVA.

## Water

The Centre is on the standard North West Water metered water tariff.

For 2001/02 fresh water costs 75.50p/m3 plus sewerage at 52.40p/m3, giving a total of 127.9p/m3.  Additionally, a meter standing charge of £700 p.a. for the 100mm meter and rateable value charge for surface water is levied at 36p/£ of rateable value.

Whilst there is no opportunity for competitive tendering, pro-active water conservation measures have been implemented including urinal cistern flush controls and percussion hand wash basin taps.

The government norm for office water usage is 7.0m3/occupant/p.a.

The water usage at the Civic Centre is a good 5.5m3/occupant so no scope to achieve water savings was determined.

# Site Management of Energy

## Responsibility

The council’s Energy Audit engineer has overall responsibility for the management of energy and water at the Civic Centre with the on site property management team responsible for efficient day to day operation of the plant.

Whilst good investment has been made in upgrading plant (the efficient gas boilers are and excellent example), the varied building types are a challenge to keep heated and ventilated whilst minimising energy usage.

Local accountability for energy usage and training would allow the site engineers to adopt a more active role in the management of energy usage.

The gas is provided via two main meters with a third sub meter connected to the Trend BMS for Phase 3.  Metering the electrical power supplies to each individual building would aid reapportionment of costs and management of energy per building.

## Reporting

The Department of Environment (DEFRA) promote Monitoring and Targeting (M&T) as the first step towards efficient energy control. The council has an effective Stark M&T system, which records the total energy usage and regular management reports of utility usage are provided.

## Conclusion

Excellent progress has been achieved to reduce energy consumption at the Civic Centre.

|  | Energy Costs | kWh |
| --- | --- | --- |
| 1999/00 | £121,910 | 3,572,533 |
| 2001/02 | £51,835 | 1,826,055 |
| % saving | 42.5% | 51.1% |

As a result the building’s energy performance compares well against similar offices. This report was commissioned to take a more in depth review to identify further saving potential.

The results of this audit is a collection of relatively small technical refinements to support the initial achievement.  However some improved conditions will result, thus substantiating the modest amount of further investment required at the Civic Centre.

Implementation of the recommendations would give an estimated cost saving of 9.4% of the 2001/2002 £51,835 utility cost and it is recommended that work proceeds on the No cost and Low Cost measures as soon as possible.

Some items have a long payback, it is our duty to identify all feasible energy saving opportunities but realistically it is only expected that those with an acceptable payback to be implemented.

ST AMBROSE BARLOW HIGH SCHOOL

When compared against the DEFRA Energy Efficiency Office national standards, the energy performance of St. Ambrose Barlow RC High School is higher than the yardsticks.

Scope to achieve cost savings both at no cost and at low cost has been determined.  These will improve the NPI, but until the main boilers are replaced and the electric night storage heating in Our Lady’s Hall the school will remain above the norm.   Some water cost savings are also identified.

Implementation of the recommendations could lead to savings estimated at £4,955 p.a. which is a useful 17% of the St. Ambrose Barlow RC High School £29,194 utility bill for a budget investment of £9,970 giving an excellent overall payback of two years.

| The potential energy savings are summarised as:- |  | Investment | Saving p.a. |
| --- | --- | --- | --- |
| No Cost | Operational changes and control adjustments | £0 | £1,070 |
| Low Cost | Rapid implementation | £9,970 | £3,885 |
| High Cost | Capital projects | Whilst replacement main boilers and gas heating for Our Lady’s Hall is desirable, these cannot be justified on simple payback. |  |
|  | Totals | £9,970 | £4,955 |

The annual energy consumption will be reduced by approximately 166,900 kWh, and will make a valuable contribution to minimising the site’s environmental impact, decreasing potential UK carbon dioxide emissions to the atmosphere by 52 tonnes of CO2 per annum (18.3%).

The calculated savings are considered conservative.  With a determined approach and careful monitoring, more savings could be realised to bring the NPI into the good sector.

CANON WILLIAMSON HIGH SCHOOL

| 1.3.1 No Cost Measures |  |  | Saving kWh | Saving £ | CO2 Tonne |  |
| --- | --- | --- | --- | --- | --- | --- |
| .1 | Electrical load – red phase heater This needs identifying |  | 9,300 day 3,800 night | 475 | 5.6 |  |
| .2 | Lighting – switch off when unoccupied |  | 8,200 day | 335 | 3.5 |  |
| .3 | Gym & Language boiler plant - Controller settings |  | 600 day 12,400 gas | 245 | 3.7 |  |
|  | Total No Cost Measures |  |  | £1,055 | 12.8 |  |

| 1.3.2 Low Cost Measures (in order of payback up to £6,000) |  | Budget Cost £ | Saving kWh | Saving £ | CO2 Tonne | Payback Years |
| --- | --- | --- | --- | --- | --- | --- |
| .1 | Main Boiler – replace defunct controls | 5,000 | 125,000 gas 600 night 2,800 day | 2,355 | 36.4 | 2.1 |
| .2 | Power regulators on refrigerators and freezers | 120 | 700 day 200 night | 35 | 0.4 | 3.4 |
| .3 | Gym & Language boiler plant ECO off control logic modification | 300 | 4,600 gas | 80 | 1.3 | 3.8 |
| .4 | Hall tungsten GLS lighting – replacement with fluorescent | 900 | 2,600 day | 140 | 1.1 | 6.4 |
|  | Total Low Cost Measures | £6,320 |  | £2,610 | 39.2 | 2.4 years |

1.3.3 	High Cost Measures

Due to the efficient plant design, no high cost measures are considered necessary.

| 1.3.4 Summary - all measures |  | Budget Cost £ | Saving kWh | Saving £ | CO2 Tonne | Pay-back |
| --- | --- | --- | --- | --- | --- | --- |
|  | Total | £6,320 | 28,800 elect. 142,000 gas | £3,665 | 52.0 | 1.7 years |

APPENDIX B

PERFORMANCE LEAGUE TABLE

| Borough Council | Improvements in Energy Efficiency 01/04/96 to 31/03/01 | Average Annual Improvement (%) |
| --- | --- | --- |
| Chester City | 21.83 | 4.30 |
| Liverpool City | 15.92 | 3.18 |
| St Helens | 12.5 | 2.50 |
| Ribble Valley | 12.33 | 2.47 |
| Copeland | 12 | 2.40 |
| Carlisle City | 10.96 | 2.19 |
| CITY OF SALFORD | 10.8 | 2.16 |
| Barrow-in-Furness | 10.15 | 2.03 |
| Knowsley | 9.8 | 1.96 |
| Macclesfield | 9.7 | 1.94 |
| Lancaster City | 9 | 1.80 |
| Warrington | 8.45 | 1.69 |
| Congleton | 8.37 | 1.97 |
| Rochdale | 8.32 | 1.66 |
| Manchester City | 7.8 | 1.56 |
| Oldham | 7.66 | 1.53 |
| Burnley | 7.62 | 1.52 |
| Trafford | 7.36 | 1.47 |
| Ellesmere Port & Neston | 7.3 | 1.45 |
| Rossendale | 7.04 | 1.41 |
| Allercale | 6.73 | 1.35 |
| Vale Royal | 6.36 | 1.27 |
| Wirral | 6.2 | 1.24 |
| Pendle | 5.86 | 1.17 |
| Sefton | 5.12 | 1.02 |
| Fylde | 5 | 1.00 |
| South Lakeland District | 5 | 1.25 |
| Wigan | 4.56 | 0.91 |
| Hyndburn | 4.25 | 0.85 |
| Bury | 4.177 | 0.84 |
| Chorley | 4.01 | 0.80 |
| South Ribble | 3.902 | 0.78 |
| Preston | 3.818 | 0.76 |
| Blackburn with Darwen | 3.59 | 0.72 |
| Crewe and Nantwich | 3.57 | 0.71 |
| West Lancashire District | 3.48 | 0.87 |
| Stockport | 3.4 | 0.68 |
| Halton | 2.92 | 0.58 |
| Tameside | 2.815 | 0.56 |
| Bolton Metropolitan | 2 | 0.40 |
| Eden District | 1.47 | 0.37 |
| Wyre | 0.78 | 0.20 |
| Blackpool | 0.63 | 0.13 |
| North West Average |  | 1.38 |