| QUALITY AND PERFORMANCE SCRUTINY COMMITTEE | 11TH DECEMBER 2000 | PART 1 (OPEN TO THE PUBLIC) |
| --- | --- | --- |
|  |  | ITEM NO. |
| SUBJECT : ENERGY MANAGEMENT ACTIVITY DURING THE PERIOD SEPTEMBER TO NOVEMBER 2000 |  |
| REPORT OF : DIRECTOR OF CORPORATE SERVICES | FOR INFORMATION |

A. REPORT SUMMARY

1.  	PURPOSE OF REPORT:

To update members on matters arising since the September 2000 meeting of the Quality and Performance Scrutiny Committee and to report recent achievements made by the Energy Management Group.

2.	RECOMMENDATIONS:

Members are asked to note the current projects in place and the level of savings being achieved and identified by the Group, and agree to a new three year programme of energy audit activity.

3.	ROUTING:

Direct to Council.

4.	IMPLICATIONS:

4.1	Resources (Finance/Staffing)	:	The operation of an efficient Energy Management Group contributes to considerable cost savings to the City Council.  Competitive tendering for energy supply will minimise the strain on limited budgets.

4.2	Performance Review	:	Not applicable.

4.3	Environmental	:	Reduction in the use of fuels, energy and water will minimise harmful effects on the environment.

4.4	Equal Opportunities	:	N/A

4.5	Community Strategy	:	N/A

4.6	Anti-Poverty Strategy	:	N/A

| IF YOU HAVE ANY QUERIES PLEASE CONTACT Jim Gosney 793 3227 | BACKGROUND DOCUMENTS |
| --- | --- |
| QUALITY CONTROL | Report prepared by Jim Gosney Checked by Donald Simpson |
| Corporate Services (Finance), Salford Civic Centre, Chorley Road, Swinton. M27 5AW |

REPORT DETAILS

5.	ENERGY MANAGEMENT

Activities undertaken during the period March to November 2000 include the following:-

Lighting, heating and water control initiatives have been implemented in a variety of premises and are summarised in Appendix A.

Energy Audit reports have been presented to the Education and Leisure, Environmental Services and Social Services Directorates and previous recommendations are being implemented at the following premises:-

Potential Annual Saving

All Hallows High School		£10,430

Joseph Eastham High School		£13,570

North Walkden Primary School		£  2,430

Radclyffe Primary School		£  3,655

Fiddlers Lane Primary School		£  4,550

St. Augustines Primary School		£  3,655

Westwood Park Primary School		£  2,540

Barton Moss Primary School		£  3,483

St. Marks C.E. Primary School		£  4,755

St. Sebastians Primary School		£  3,750

Summerville Primary School		£  5,340

Bridgewater Primary School		£  5,842

Westwood Park Nursery Centre		£  2,500

Dorning St. Nursery		£  1,100

Crompton House		£  7,800

Recommendation Tables and  management summaries in respect of these completed audits are attached in Appendix B.

The potential annual savings identified during the review period amount to £75,400 an average pay back period for the implementation cost of 18 months.

Detailed audits of Irwell Park High, The Friars and St. Pauls Primary Schools and The Magistrates’ Court are on-going and reports will be issued on completion.

An application has been submitted for external funding for a feasibility study for a Combined Heat and Power (CHP) scheme at the Clarendon Area of the City in conjunction with the Director of Housing.

During the period under review the energy audit team have committed a sum of £132,917 consists of approximately:-

Lighting Controls	£40,026

Water Controls	£14,202

Heating Controls	£76,694

A full breakdown of expenditure is in Appendix A.

6.	EXTERNAL FUNDING

Members will recall that applications to the school Energy Programme (managed by CREATE) on behalf of 6 primary schools and one high school have been successful.  Further applications were submitted on behalf of St. Sebastian’s, Bridgewater Primary School and All Hallows during the period under review and were also successful.

External funding of the order of £28,000 has been received which is being used for further energy savings initiatives.

With the assistance of the Energy Audit Team each school has established an energy policy and a three-year strategy to progressively reduce consumption.

The funds which have been authorised, when combined with the monies made available by the schools and a contribution from the energy audit budget, will allow the installation of new controls on heating, lighting and water consumption.

7.	ENERGY AUDIT THREE YEAR PROGRAMME

Details of projected savings are in Appendix C.  A new three-year programme has been developed to achieve these savings and is submitted for approval.  Details are in Appendix D.

APPENDIX A

EXPENDITURE DETAILS

ENERGY AUDIT ACTIVITIES - APRIL 2000 TO NOVEMBER 2000

| PREMISES | COST £ | WORK COMPLETED ONGOING |
| --- | --- | --- |
| Lighting Controls North Walkden Primary Barton Moss Primary Fiddlers Lane Primary St. Augustines Primary Westwood Park Primary Radclyffe Primary Cadishead Recreation Centre Pendlebury Recreation Centre All Hallows High School Bridgewater Primary Eccles Recreation Centre St. Sebastians | 2,376 3,508 2,205 3,815 3,538 6,781 178 278 10,856 2,976 949 2,566 40,026 | 05.05.00 04.04.00 14.04.00 20.04.00 04.05.00 04.05.00 28.07.00 28.07.00 25.08.00 25.08.00 29.08.00 On-going |
| Water/Urinal Controls Grosvenor Road Bridgewater Primary Friars Primary Barton Moss Primary Radclyffe Primary Westwood Primary North Walkden Primary Fiddlers Lane Primary Cleavely Track All Hallows High School Cadishead Recreation Centre St. Sebastians | 1,959 1,343 973 2,309 1,190 757 752 1,194 707 1,673 225 1,120 14,202 | 13.07.00 02.05.00 04.05.00 04.05.00 09.05.00 08.05.00 31.05.00 02.10.00 11.09.00 On-going |
| Boiler Plant Controls/Heating Controls Civic Centre Phase 1 Civic Centre Phase 2 Pendlebury Recreation Centre St. Patricks High School Little Hulton High School Bridgewater Primary Swinton High School Walkden High School Irlam & Cadishead Buile Hill High Irlam Pool | 3,222 6,690 20,706 6,969 4,189 4,284 7,050 3,864 3,750 4,980 10,990 76,694 | 31.03.00 31.05.00 31.05.00 06.09.00 06.09.00 29.11.00 10.09.00 01.09.00 04.10.00 03.10.00 On-going |
| Training Course Stark Monitoring System | 1,500 |  |
| Water Surveys/Leak Detection Turnpike House/Leak Detection | 495 | Ongoing |

Committed Total Expenditure  =  £132,917

APPENDIX D

ENERGY AUDIT PROGRAMME 2001-2004

It is planned to conduct energy audits of the more energy intensive buildings, requests have been received for full audits of Primary Schools,  High Schools, Leisure Centres and Sports Halls, Libraries, Youth Clubs and administration centres.

The approved energy audit development plan has identified potential savings in the buildings under review of the order of £250,000 per annum.

The objective of the proposed programme is to reduce energy consumption in the Authority’s buildings in the next three years 2001-2004 by 8% financial value of £400,000 and thereafter to submit a further programme for consideration.

The audits will be carried out in two stages;

Firstly to collate usage information and calculate actual performance against benchmark performance figures ranking buildings in performance.

The premises that appear in the poor performance category will be the ones selected for the first year of a three year programme.

The second stage will be to conduct energy audits and make recommendations that will improve energy efficiency at each of the premises showing the payback periods.

The environmental impact of each scheme will be assessed and taken into consideration before implementing.

Year One				Time Allocated

| Education Premise Energy Audits/Survey 30 Premises |  | 150 Days |
| --- | --- | --- |
| Leisure Audits 10 Premises |  | 40 Days |
| Social Services 10 Premises |  | 30 Days |
| Education Centre |  | 3 Days |

| Education Offices Civic Centre Complex Environmental Services 10 Premises Eccles Town Hall Arts/Leisure 10 Sites Housing 10 Sites |  | 4 Days 10 Days 30 Days 4 Days 40 Days |
| --- | --- | --- |
| 30 Days Review District Heating Tariff Rates and Contracts as supplied by AHS Emstar - Housing and make recommendations to reduce costs Arrange training for building users/caretakers to advise on energy efficiency measures Produce and present reports and implement proposals from energy audits 84 audits - one and half days each |  | 20 Days 10 Days 126 Days |
| Conduct feasibility studies for the potential benefits of the installation of combined heat and power systems for Leisure and Housing premises - and produce reports |  | 40 Days |
| Prepare tender documentation for purchase of Gas and Electricity |  | 29 Days |
| Project manage and implement the existing programme of low energy lighting water savings schemes and pool cover installations supervise and liaise with clients and contractors |  | 30 Days |
| Carry out desk top analysis of water consumption checking for likely errors checking consumption relative to the size of meter and check by site survey that the client is paying only for the services received and make recommendations for control of domestic use e.g. urinals and leakage from underground pipework. From this analysis it is proposed to formulate a rolling programme of visits to at least 50 premises. |  | 50 Days |
| Investigate and advise on Performance Contracting, the use of consultants, P.F.I. opportunities and external funding applications |  | 10 Days |
| Advise on energy efficient design of new buildings and the choice of fuel and equipment selection in boiler replacement programmes for all clients |  | 10 Days |
| Attend Energy Managers Group Meetings at other Local Authorities Prepare Annual Energy Report Reactive, response to enquiries and request from clients |  | 20 Days 4 Days 40 Days |
| TOTAL |  | 730 Days |

Year Two Programme

|  | Time allocated |
| --- | --- |
| Education Premises Energy Audits/Surveys 30 premises Arts/Leisure | 150 days 40 days |
| Leisure Audits 10 premises | 40 days |
| Social Services 10 premises | 30 days |
| Housing - Energy Audit 10 premises Environmental Services 10 premises | 30 days 30 days |
| Training for building users/caretakers to advise on energy efficiency measures | 20 days |
| Produce reports and implement proposal from energy audits 70 audits - 1½ days each | 105 days |
| Project manage energy saving proposals | 70 days |
| Desk Top analysis of water consumption | 50 days |
| Project manager water programme | 10 days |
| Investigate and advise PFI opportunities, performance contracting consultants and external funding submissions | 10 days |
| Advise on energy efficient design of new buildings and the choice of fuel and equipment selection in boiler replacement programmes for all clients | 25 days |
| Attend Energy Managers Group Meetings at other Local Authorities | 20 days |
| Prepare Energy Reports | 10 days |
| Reactive response to enquiries and requests from client departments | 40 days |
|  | 730 DAYS |

Year Three Programme

|  | Time allocated |
| --- | --- |
| Revisit and continue rolling programme of energy audits 30 premises | 150 days |
| Leisure Audits 10 premises | 40 days |
| Social Services 10 premises | 30 days |
| Housing 10 premises | 30 days |
| Administration premises 4 premises | 8 days |
| Environmental Services 10 premises | 30 days |
| Arrange training for building uses/caretakers to advise on energy efficiency measures | 20 days |
| Produce and present reports and implement proposals from energy audits 70 audits - one and half days each | 105 days |
| Monitor and continue CHP programme | 40 days |
| Project manage energy savings proposals | 70 days |
| Desk Top analysis of water consumption leading to rolling programme of visits to at least 50 premises | 58 days |
| Project manager water programme | 10 days |
| Advise client departments of energy efficient design and choice of fuel | 25 days |
| Attend Energy Managers Group Meetings at other Local Authorities | 20 days |
| Prepare an Annual Report | 14 days |
| Reactive response to enquiries and request from clients | 40 days |
|  | 730 DAYS |

DIMENSIONS

Annual fuel budget	£4,400,000

Energy Saving Work	£150k (varies from year to year)

Staff	(i)	Energy Manager

(ii)	2No  Energy Officers

1No  Energy Auditor

1No  Technical Assistant

STATISTICS

Buildings involved	550

Electricity supplies at	550 premises

Oil supplies to	  93 premises

Gas supplies to 	400 premises

Water supplies	600 premises

estimated average annual request for advice		650 P.A.

anticipated average number of visits to site		400 P.A.

APPENDIX C

ENERGY AUDIT DEVELOPMENT - PROJECTED SAVINGS

|  | Maximum £k pa | 2000/01 £k pa | 2001/02 £k pa | 2002/03 £k pa | 2003/04 £k pa |
| --- | --- | --- | --- | --- | --- |
| Cost Reductions/Savings 1. Water Leakage/Control 2. Combined Heat and Power (CHP) 3. Increased Energy Audit Activity 4. Good Housekeeping 5. Energy/Water Retendering | 105 100 150 155 200 | 50 0 50 50 100 | 55 35 100 100 100 | 105 70 150 155 200 | 105 70 150 155 200 |
| Total | 710 | 250 | 490 | 680 | 680 |
| External Funding CHP Capital Grants CREATE Climate Tax Levy Reduction New Deal P.V. Cells |  |  |  |  |  |
| Total | 335 | 135 | 200 |  |  |
| Additional Costs Staffing CHP Capital Additional "pump priming" | 56 300 100 | 50 56 56 56 - Fund from capital programme - Fund from capital programme |
| Total | 456 === |  |

APPENDIX B

RECOMMENDATION TABLE/MANAGEMENT SUMMARY

DORNING ST. NURSERY CENTRE

| Premise | Description of Recommendations | Main Utility Saved | Annual Saving (£) | Estimated cost of implementation (£) | Pay Back Period (Years) | Reduction of CO2 (Tonnes) |
| --- | --- | --- | --- | --- | --- | --- |
| HOUSEKEEPING 1 | Commit to "A Whole School Approach" | Oil, Water Electricity | 524 | Nil | Immediate | 10.4 |
| BUILDING FABRIC 2 | Consider improving the thermal performance of the building to at least current Building Regulations at all opportunities particularly during any refurbishment works. | Oil | Long term savings and improvement in comfort levels would be realised. |
| 3 | Install draught exclusion to all external doors and openable windows | Oil | Long term savings and improvement in comfort levels would be realised. |
| CENTRAL PLANT 4 | Review control settings | Oil | Ensuring efficiency of fuel use centrally will realise beneficial savings. |
| 5 | Modify plant to heat hot water calorifier off LPHW system | Elec | 956 | 900 | <13 months | 9.8 |
| HEATING 6 | Clear obstructed radiators | Oil | 90 | Nil | Immediate | 1.7 |
| LIGHTING 7 | Install occupancy controls to where practicable. Switch off remaining lights when not required. | Elec | 230 | 1,100 | 4.8 | 2.4 |
| 8 | Overhaul lighting (long term), replace existing 38mm fluorescent with new 26mm high frequency fluorescent. Replace filaments lamps with compact fluorescent | Elec | High capital cost offset by long term savings. Also improved quality of light and teaching environment. |
| DOMESTIC HOT WATER | Insulate all DHW pipeworks | Elec, Oil | 120 | 900 | 7.5 | 2.2 |

RECOMMENDATION TABLE/MANAGEMENT SUMMARY

CROMPTON HOUSE

| Premise | Description of Recommendations | Main Utility Saved | Annual Saving (£) | Estimated cost of implementation (£) | Pay Back Period (Years) | Reduction of CO2 (Tonnes) |
| --- | --- | --- | --- | --- | --- | --- |
| METERING 1 | Sustainable reductions in energy and water use can only be achieved if the users are responsible for the costs. Install comprehensive sub-metering for all utilities. | Electricity, Gas, Water | Although sub-metering does provide direct savings, per se, off-charging will incentivise users to carry out 'good housekeeping’. |
| HOUSEKEEPING 2 | Typically between 5-25% can be saved through good housekeeping. | Electricity, Gas, Water | 2,200 | Nil | Immediate | 29.3 |
| BUILDING FABRIC 3 | All opportunities to improve the thermal performance of the buildings should be considered, particularly during any major remodelling works to the buildings. Such measures may include installing or upgrading insulation, installing double glazing, draught proofing doors and windows, installing auto door closures to external doors, installing measures to reduce solar gain for greater summertime comfort. Expose the higher thermal capacity concrete structures of the building. |
| CENTRAL PLANT 4 | Review boiler control system settings | Gas | 950 | Nil | Immediate | 21.9 |
| 5 | Install optimiser control of the heating plant | Gas | 400 | 1,200 | 3 | 9.2 |
| 6 | Review control of archive heater | Gas | 200 | Nil | Immediate | 4.6 |
| 7 | Review control settings for computer server room cooling plant | Dependent upon the findings of the review. Manufacturers declared operating temperatures for I.T. equipment should be accounted for. |
| 8 | Reposition outside air temperature sensor | Improvements in comfort and improved control of the heating. |
| VENTILATION 9 | Link toilet fans to any new lighting controls. See recommendation 16. | Electricity | 200 | As part of lighting controls installation | N/A | 2.2 |
| 10 | Review requirements and control of ducted ventilation to Food Control dept. | Electricity | Savings could be achieved through removing the fan altogether or improving the existing controls. |
| 11 | Remove portable fans from use once underlying factors for their use have been addressed. | Electricity | 250 | Nil | Immediate | 2.8 |
| SPACE HEATING 12 | Consider modifying existing heating zones to accommodate North/South differential temperatures. | Gas | A costly exercise. However, this should be considered at any time of refurbishment. |
| 13 | Review space temperature control regime - consider installing space temperature sensors. | Local control of space temperature could be improved by installing space temperature sensors. When combined with TRV’s, could help minimise differential temperatures and improve comfort. Existing controls capacity for new sensors to be established. To be considered only if insufficient effect from adjusting control parameters. |
| 14 | Consider insulating exposed heating pipework. | Gas | The pipework is part of the heat delivery to the office space. The existing control regime should be reviewed before this is considered. |
| 15 | Consider installing additional TRV’s where appropriate e.g. south facing accommodation. | Gas | 350 | 1,950 | 5.6 | 8.0 |
| LIGHTING 16 | Consider installation of automatic lighting controls. | Electricity | 2,800 | 13,500 | 4.8 | 31.2 |
| 17 | Replace tungsten filament lamps with compact fluorescent | Electricity | 60 | Nil - Free from Energy Audit | Immediate | 0.7 |
| 18 | Install reflective film to south facing windows | Electricity, Gas | 362 and improved comfort | 3,600 | 10 | 6.4 |
| 19 | Consider installing solar shading and/or light shelves to south face of building | Electricity, Gas | A costly exercise. However, this should be considered at any time of refurbishment. Greater benefits realised compared to solar film. |
| HOT WATER 20 | Install 7-day timeclocks to hot water heaters | Electricity | 850 | 1,100 | 1.3 | 9.5 |
| OFFICE EQUIPMENT 21 | Switch off when not required. Utilise energy saving stand-by facilities during daily use. Purchase energy efficient equipment. Utilise electronic mail rather than use of facsimile. See Appendix A. | Electricity | 850 Dependent upon the management process | Nil | Immediate | 9.5 |
| WATER 22 | Install push taps | Water | 210 | 670 | 3.2 | - |
| OTHER 23 | Rationalise use of domestic appliances | Electricity | 100 | Nil | Immediate | 1.1 |
| 24 | Install Sava Plugs to fridges and freezers and review appliance thermostat settings | Electricity | 110 | 180 | 1.6 | 1.1 |
| 25 | Remove Electric Heaters | Electricity | 258 | Nil | Immediate | 2.9 |

APPENDIX D

SAVINGS IDENTIFIED

| Site Name | Recommendation | Potential Saving |
| --- | --- | --- |
| Higher Irlam Library | Refund for overcharge on R51 Units | £4,261.51 |
| Sports Changing Rooms, Cleggs Lane | MD1.N to Economy 7 | £3,196.63 |
| Vulcan House | Re-Tender | £1,110.00 |
| Princes Park Garden Centre | Overcharge on redundant meters | £5,457.53 |
| Cultural Tender | Obtain competitive prices | £1,946.00 |
| Social Services Tender | Obtain competitive prices | £14,319.00 |
| Catering Tender | Obtain competitive prices | £719.00 |
| Recreation Tender | Obtain competitive prices | £6,432.00 |
| Walkden Library | Install time clock on heating |  |
| Launching Strip STH Bay Dock | MD1.N to General Purpose (G13) | £488.00 |
| Pendleton Business Centre | Av Cap Reduction (80-34) | £651.36 |
| Broadwalk Resource Centre | Av Cap Reduction (120-51) | £977.04 |
| Vulcan House | Energy Audit |  |
| 136 Premises | Re-tender maximum demand electricity sites | £100,000 |

TOTAL SAVINGS  £139,545